CORAYVAC® CLASSIC SF INFRARED RADIANT HEATERS

PRODUCT SPECIFICATIONS

SYSTEM

- General

1. Condensing System:  Design gas-fired radiant systems to operate such that water vapor present in products of combustion will be condensed, and this heat of condensation will be extracted by the system and will be added to the heated space.

2. Vacuum Vented:  To preclude the possibility of combustion gases escaping into the building, the entire system must be under a negative pressure at all times and vented to the outside atmosphere.

- Codes and Standards

1. American National Standard / CSA Standard Gas-Fired Low Intensity Infrared Heaters:

a. Construct and certify gas-fired infrared heaters in accordance with latest edition ANSI Z83.20 / CSA 2.34 "Gas-Fired           Low-Intensity Infrared Heaters" including all current supplements.

2. Installation Compliance: United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 - latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 - latest revision.

3. CSA Compliance: Provide CSA Seal affixed to each burner name plate and provide CSA Certification of heater design as vented or unvented infrared heater for indoor installation.

4. National Standard Gas Piping Compliance: Install and connect gas piping to gas fired infrared heaters in accordance with United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 - latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 - latest revision.

5. National Electrical Code Compliance: Install and connect electrical wiring to gas fired infrared heaters in accordance with: 1.) United States: Refer to National Electrical Code®, NFPA 70 - latest revision. Wiring must conform to the most current National Electrical Code®, local ordinances and any special diagrams furnished. 2.) Canada: Refer to Canadian Electrical Code, CSA C22.1 Part 1 - latest revision.

6. Venting: Venting shall be installed in accordance with the requirements within the manufacture installation operation and service manual and in compliance with United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 – latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 – latest revision.

7. Compressed and Liquefied Natural Gas Installation: Installation must comply with Code for Motor Fuel Dispensing Facilities and Repair Garages NFPA 30A – latest revision. Heaters are certified by CSA to meet maximum tube temperature of 750°F (399°C) in accordance with NFPA 30A (2012 edition) section 7.6.6.

6. National Performance Rating for Gas Fired Infrared Heaters Standard: Radiant output of gas fired infrared heaters shall be rated in accordance with AHRI Standard 1330.  Refer to Performance Rating for Radiant Output of Gas Fired Infrared Heaters Standard CAN/ANSI/AHRI 1330-2015.

EQUIPMENT

A. Burner Box

1. (Natural Gas) (Propane) model, burner assemblies consisting of heavy duty cast iron burner heads, other substitutions will not be accepted. Pre-wired gas controls with direct spark ignition module, and combustion air filters supplied. Provide minimum numbers of burners indicated to insure proper radiant heat distribution.  Fewer burners of larger capacity will not be accepted. Burners shall be designed for firing in tandem without adverse effects from combustion gases from upstream burners. Burners shall be CSA certified to be in compliance NFPA 30A (2012 edition) section 7.6.6.

2. Design firing rate of burners shall be XXXXXXX Btu's per hour as stated on drawings. Clearances to a combustibles surface as measured from the tube surface shall not exceed XX" above, XX" below, XX" on each side.

3. Premix Gas and Air:  Provide burners to totally pre-mix air and gas required for combustion.

4. Constant Air/Gas Ratio:  Provide burners designed to maintain constant proportion of fuel gas to filtered combustion air. Introduce both fuel gas and air at atmospheric pressure, and establish flow of both by means of negative pressure on the downstream side of the flow metering orifices.  Design so that if combustion air flow is impeded for any reason, gas flow rate will decrease in constant proportion to maintain proper gas/air mixture for complete combustion.

B. Burner Controls

- Factory Wired: All burners shall be factory wired for 115 VAC with transformer for 24 VAC DSI operation and supplied with a grounded 24-30 inch (61–76 cm) three wire pigtail located at rear of burner

2.	Fail-Safe Controls: To assure a high degree of fail-safe operation, the design shall preclude main flow of gas 	if any or all of the following abnormal conditions occur:

a. Power fails (Gas valves in burners close in safe position).

b. Main Valve fails in open position

c. Vacuum pump motor fails (Vacuum proving switch cuts power to burners).

3. Ignition Controls: All gas vacuum-firing burner units shall be equipped with a Direct Spark Ignition Module (DSI).  The DSI module shall have a 15-second flame safety time per ignition trial before lockout occurs.  In addition, the DSI module shall be capable of a minimum of 3 trials for ignition to provide maximum reliability.

C. Vacuum Pump

Vacuum Pump 1/3 HP Option:

  - Outdoor Venting:  The system shall vent all products of combustion outdoors by means of the vacuum pump.

  - Motor:  Vacuum pump shall be equipped with a 1/3 horsepower, 60 hertz, 120/230 volts AC, 3450 RPM, single phase motor.  This motor shall have thermal overload protection, high temperature sealed ball bearings, and shall be constructed in accordance with electric motor industry standards.

  - Housing:  The scroll of this pump shall 12-gauge stamped steel construction.  The impeller wheel shall be pressure cast 319-alloy aluminum with a minimum metal thickness of approximately 3/32 inch (.24 cm).

  - Pressure Switch:  As an additional safety measure, there will be a low voltage (24 VAC) interlock circuit from the pressure switch (located at the inlet to the vacuum pump) to the controller to prove pump operation.

  - High Temperature Acoustical Isolation:  The vacuum pump shall be acoustically isolated from the system with a flexible connector with a constant service temperature rating of 350ºF (177°C) minimum.  The connection between the 4” (10 cm) pump inlet and tailpipe is made with acoustic boot and clamps provided.  The discharge connection is made with an acoustic boot and schedule 40 steel pipe or 4 inch (10 cm) ABS schedule 5 pipe and fittings.  The motor in the vacuum pump shall be secured with rubber mounts for acoustical isolation.

  - Rotation:  Vacuum pump motor requires a grounded circuit 120/230 volts AC, single phase, 60 hertz for a maximum of 4.8/2.4 full load.  This motor must have the same rotation to match the direction of the arrow on the fan scroll.  If the motor is not rotating in this direction, it must be reversed by interchanging the black and red line leads as shown on the motor nameplate.

Vacuum Pump 3/4 HP Option:

- Outdoor Venting:  The system shall vent all products of combustion outdoors by means of the vacuum pump.

- Motor:  Vacuum pump shall be equipped with a 3/4 horsepower, 60 hertz, 208-230/460 volts AC, 3450 RPM, three phase motor.  This motor shall have thermal overload protection, high temperature sealed ball bearings, and shall be constructed in accordance with electric motor industry standards.

- Motor:  Vacuum pump shall be equipped with a 3/4 horsepower, 60 hertz, 120/230 volts AC, 3450 RPM, single phase motor.  This motor shall have thermal overload protection, high temperature sealed ball bearings, and shall be constructed in accordance with electric motor industry standards.

- Housing:  The scroll of this pump shall be cast iron with a minimum metal thickness of approximately 3/16 inch (.48 cm).  The impeller wheel shall be pressure cast 319-alloy aluminum with a minimum metal thickness of approximately 3/32 inch (.24 cm).

- Pressure Switch:  As an additional safety measure, there will be a low voltage (24 VAC) interlock circuit from the pressure switch (located at the inlet to the vacuum pump) to the controller to prove pump operation.

- High Temperature Acoustical Isolation:  The vacuum pump shall be acoustically isolated from the system with a flexible connector with a constant service temperature rating of 350ºF (177°C) minimum.  The connection between the 4.5” (11 cm) pump inlet and tailpipe is made with acoustic boot and clamps provided.  The discharge connection is made with an acoustic boot and schedule 40 steel pipe or 4 inch (10 cm) ABS schedule 5 pipe and fittings.  The motor in the vacuum pump shall be secured with rubber mounts for acoustical isolation.

- Rotation:  Vacuum pump motor requires a grounded circuit 208-230/460 volts AC, three phase, 60 hertz for a maximum of 2.5 full load amps via a variable frequency drive.  This motor must have the same rotation to match the direction of the arrow on the fan scroll.  If the motor is not rotating in this direction, it must be reversed by interchanging any 2 line leads as indicated on the motor nameplate.

- Rotation:  Vacuum pump motor requires a grounded circuit 120/230 volts AC, single phase, 60 hertz for a maximum of 6.6 full load amps.  This motor must have the same rotation to match the direction of the arrow on the fan scroll.  If the motor is not rotating in this direction, it must be reversed by interchanging the black and red line leads as indicated on the motor nameplate.

- Speed Control:  Vacuum pump motor speed and power supply shall be from a 3/4 HP (208-230/460V) three phase or 1HP (120/230VAC) single phase variable frequency drive.   Variable frequency drive power input shall be specified as either 120/230VAC, 1 ph, 60 Hz, 16.6A; or 208-230/460V, 3 ph, 60 Hz, 6.9A.  Variable frequency drive output frequency shall control the speed of the vacuum pump motor by speed reference following analog signal.

Vacuum Pump 2 HP Option:

- Outdoor Venting:  The system shall vent all products of combustion outdoors by means of the vacuum pump.

- Motor:  Vacuum pump shall be equipped with a 2 horsepower, 60 hertz, 208-230/460 volts AC, 3450 RPM, three phase motor.  This motor shall have thermal overload protection, high temperature sealed ball bearings, and shall be constructed in accordance with electric motor industry standards.

- Motor:  Vacuum pump shall be equipped with a 2 horsepower, 60 hertz, 208-230 volts AC, 3450 RPM, single phase motor.  This motor shall have thermal overload protection, high temperature sealed ball bearings, and shall be constructed in accordance with electric motor industry standards.

- Housing:  The scroll and impeller wheel of this pump shall be 3 mm welded steel construction.

- Pressure Switch:  As an additional safety measure, there will be a low voltage (24 VAC) interlock circuit from the pressure switch (located at the inlet to the vacuum pump) to the controller to prove pump operation.

- High Temperature Acoustical Isolation:  The vacuum pump shall be acoustically isolated from the system with a flexible connector with a constant service temperature rating of 350ºF (177°C) minimum.  The connection between the 6” (15 cm) pump inlet and tailpipe is made with acoustic boot and clamps provided.  The discharge connection is made with an acoustic boot and 6” (15 cm) pipe and fittings.

- Rotation:  Vacuum pump motor requires a grounded circuit 208-230/460 volts AC, three phase, 60 hertz for a maximum of 5.5 full load amps via a variable frequency drive.  This motor must have the same rotation to match the direction of the arrow on the fan scroll.  If the motor is not rotating in this direction, it must be reversed by interchanging any 2 line leads as shown on the motor nameplate.

- Rotation:  Vacuum pump motor requires a grounded circuit 208-230 volts AC, single phase, 60 hertz for a maximum of 12.8 full load amps.  This motor must have the same rotation to match the direction of the arrow on the fan scroll.  If the motor is not rotating in this direction, it must be reversed by interchanging the specified line leads as shown on the motor nameplate.

- Speed Control:  Vacuum pump motor speed and power supply shall be from a 2 HP (230/460V) variable frequency drive.   Variable frequency drive power input shall be specified as 208-230/460, 3 ph, 60Hz, 5.8A.  Variable frequency drive output frequency shall control the speed of the vacuum pump motor by speed reference following analog signal.

D. Reflectors – High Efficiency

Provide high radiant reflective aluminum reflectors installed over all heat exchanger tube.  Provide wide parabolic design reflector with 12 reflective surfaces that when tested with select models* can enhance model to an Infrared Factor (IF) of 15 when tested in accordance to AHRI standard 1330 (latest edition) for Radiant Output of Gas Fired Infrared Heaters.  Reflector shall reflect 100% of the infrared energy that it receives from the heat exchanger tube directly to the floor.  Reflectors with less than 12 reflective surfaces shall not be allowed.  In order to maximize radiant output and reduce convective heat losses, reflectors are to extend below the bottom of the heat exchanger tube.  Provide continuous reflector over all tube and fitting heat exchanger surfaces.  Provide reflector end caps as necessary to reduce convective heat losses.

*Multiple models rated in accordance with AHRI Standard 1330 have achieved an Infrared Factor (IF) of 15, models included: CTH2-100 @ 30’ tested with straight orientation, HRS & HT Aluminized tubing with high efficiency reflector.

Reflectors - Standard

Provide high radiant reflective aluminum reflectors installed over all heat exchangers.  Provide reflector joint pieces over heat exchanger fittings such as elbows so reflector covers heat exchanger continuously.  In order to maximize radiant output and reduce convective heat losses, reflectors are to extend below the bottom of the heat exchanger tube.

- Cover Elbow Fittings: Provide reflector joint pieces over heat exchanger elbows so reflector covers heat exchanger continuously.

- End Cap Fittings: All reflectors at end of the heat exchanger pipe and any elbows joints shall have end caps to prevent convective heat from escaping.

- Side Reflectors: System to have perimeter side extension reflector in certain areas of layout as shown on plan where specified.  Side reflectors permanently attach to side of top reflector and are secured to the pipe by three side reflector supports and two "Z" clips for each 8’ (2.44 m) section of side reflector.  To prevent convection losses, tilting of reflectors will not be acceptable.

- Over Entire pipe Network: Standard reflectors shall be installed on all radiant pipe and tail pipe as indicated on system layout furnished.

E. Outside Air

Provide fresh outside air to supply each burner and end vent for the support of combustion air as called for on plans.  Fresh outside air supply must be installed in accordance with the requirements within the installation operation and service manual.

- Outside Air Blower: Blower shall be 167 watt, 60 hertz, 120 volts AC, 3000 RPM, single phase motor.  Provides system with pressured outside air supply to each burner and end vent for the support of combustion air as called for on plans.

- Fresh Air Filter Box: System shall be equipped with fresh air filter box providing pre-filtered outside air through 1” thick E-Z Kleen® aluminum mesh filters, or equivalent.  Filter box to be constructed of 22-gauage galvanized steel with 8” (20 cm) inlet and outlet as per the manufacture of the infrared system specifications.  The fresh air filter box must be installed in accordance with the requirements within the installation operation and service manual.

F. Controls

- Thermostats: Provide where indicated, line voltage or low voltage type connected to infrared heater. Mount thermostat 5’ – 6’ (1-2 m) above finish floor or as otherwise noted on the drawing. All thermostats shall be numbered instead of marked in degrees and shall not have thermometers.

- ROBERTS GORDON® System Control: Provide where indicated, a single control panel capable of managing four zones of burners’ temperature control and power. The control will also give power output to as many as two pumps, provided that the load is not greater than 20 A and 1 Ø.  The control panel shall have indicator lights showing: Line Power, Pump 1 Power, Pump 2 Power, Pressure Switch 1 Power, Pressure Switch 2 power and 4-Zones. The panel shall include a 24 VAC power supply to supply power to electronic thermostats and shall be capable of using mechanical thermostats equipped with a heat anticipator.  The control panel enclosure shall be painted steel and shall include indicator lights to display when line power is available to the panel, when the vacuum pumps are energized, when the vacuum proving switches are closed and when the burner zone relays are energized.  The control panel shall have separate line voltage and low voltage terminal strips for ease of wiring.  The control panel shall be manufactured by the same manufacture as the infrared burners and vacuum pumps for single-source accountability.

G. Infrared Piping – Radiant Piping - Heat Exchanger

- Radiant Tube: Shall be new schedule 40 ASTM A53 (Latest edition) grade B ERW black steel pipe TNC 4” (10 cm), both ends threaded to 4” (10 cm) NPT conforming to ANSI/ASME B1.20.1 (Latest edition).

- Tail Pipe Tube: Shall be new schedule 40 ASTM A53 (Latest edition) grade B ERW black steel pipe TNC 4” (10 cm), both ends threaded to 4” (10 cm) NPT conforming to ANSI/ASME B1.20.1 (Latest edition). Shall be 4 in. (10 cm) Porcelain Coated steel tube X 16 gauge wall with an emissivity factor of 0.90 or greater.

- Radiant Tube Fittings: Shall be 150 lb. malleable black iron 4” (10 cm), both ends threaded to 4” (10 cm) NPT conforming to ANSI/ASME B1.20.1 (Latest edition).

- Tail Pipe Tube Fittings: Shall be 150 lb. malleable black iron 4” (10 cm), both ends threaded to 4” (10 cm) NPT conforming to ANSI/ASME B1.20.1 (Latest edition).  (Porcelain Coated steel X 16 gauge wall). For tubes as described in the installation, operation and service manual.

- Hanging Materials: All system’s tube must be supported in accordance with best building practices, local codes, seismic requirements, and applicable standards and as shown on plans. Pipe shall pitch down at least ½” in 20’ (1.27 cm in 6.1 m) on radiant lines and 1” in 20’ (1.27 cm in 6.1 m) on tailpipe lines toward the vacuum pump.

- End Vent Assembly: Each open end combustion chamber shall have an approved end vent with fresh air connected for the support of combustion air and the reflector shall terminate with an end cap, and be installed according to manufacturer’s installation operation and service manual and as shown on plans.

- Condensate Piping: Above Ground:  copper tubing type M hard drawn. Fittings: ANSI/ASME 816.23 cast brass or ANSI/AMSE 816.29, wrought copper.  Joints ANSI/ASTM B32, solder, grade 95TA.

- Condensate Neutralization Tube: Provide and install condensate neutralization tube as per the manufacture instructions in the installation operation and service manual.

INSTALLATION OF GAS FIRED INFRARED HEATERS

A. General

Install gas fired infrared heaters as indicated, in accordance with manufacturer's installation operation and service manual and in compliance with applicable codes and approvals.  Allow adequate space for servicing or removal of the unit without disturbing other piping or equipment.

B. Support

Suspend heat exchanger, burner, gas piping, conduit, and reflectors from building substrate as indicated, or if not indicated, in manner to provide durable and safe installation; and in accordance with manufacturer's installation operation and service manual.  Mounting height to be a minimum         feet (_____ m) from floor level.

C. Clearances to Combustibles

Always maintain clearance to combustibles as outlined and printed on burner nameplate and in manufacturer's product data.  Measure clearance distance from surface of heat exchanger or as indicated by approval agency's listing.

D. Venting

Install vent piping as indicated on plans.  Terminate where indicated on the drawings with a vent terminal assembly as supplied by the manufacturer. The venting must be installed in accordance with the requirements within the installation operation and service manual and the following codes: United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 - latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 - latest revision.

E. Gas Piping

Install gas piping as indicated and in accordance and in compliance with applicable codes and approval: United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 - latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 - latest revision.

- Required Gas Supply Inlet Pressures:

# Natural Gas Units	Required Minimum Gas Pressure	Maximum Gas Pressure

20,000-80,000 Btu/h	4.5” wc	14” wc

# Propane Gas Units	Required Minimum Gas Pressure	Maximum Gas Pressure

40,000-80,000 Btu/h	10.5” wc	14” wc

- Local Codes: Gas supply piping must meet local requirements and be sized in accordance with Btu/h demand, available pressure and total length of supply line required for the installation.  Connection from supply line to burner unit must be made in accordance with installation operation and service manual.  Gas shut-off cock, as supplied with unit, and controls in unit must not be subjected to more than 1/2 lb. or 14” wc pressure.

- Drip Legs: Provide drip legs at all gas risers.

F. Electrical Wiring

Install electrical wiring as indicated. Connect power wiring to burners and vacuum pumps, control wiring between burners, vacuum pump, control panels, thermostats, timers, relays and transformers in accordance with manufacturer’s wiring diagrams.

H. Thermostats

Provide where indicated, 24VAC thermostat, connected to control system.  Mount thermostat 5’ 6” (1.67 m) above finish floor or otherwise as noted on the drawing. Low voltage thermostats shall be numbered instead of marked in degrees and shall not have thermometers. Low voltage wiring must follow local codes.

FIELD QUALITY CONTROL

A. Start-Up

Start-up, test, measure tube surface temperatures and adjust inlet gas pressure in accordance with manufacturer's start-up instructions in the installation operation and service manual, and Utility Company's requirements.  Return Start-Up and Installation Report to the manufacture within 24 hours of system start-up as indicated in the installation operation and service manual. Check and calibrate controls.  Burners are calibrated by the manufacture and must not be adjusted.

CLOSEOUT PROCEDURES

A. Training

Provide services of manufacturer's technical representative to instruct operating personnel in operation and maintenance of gas fired infrared heaters.

1. Schedule instruction with operating building owner, provide at least 7 days notice.

WARRANTY

Provide written warranty, by manufacturer, agreeing to replace/repair, within warranty period, components of gas fired infrared systems furnished by manufacturer, which are defective in either material or workmanship, provided manufacturer's instructions for handling, installing, protecting, and maintaining units have been adhered to during warranty periods follows:

A. Three (3) year warranty on the burner system from the date of final acceptance of the infrared heaters.
      B. Twenty Five (25) year warranty from the date of final acceptance of cast iron combustion chambers.

C. Twenty Five (25) year warranty from the date of final acceptance of 3/4 HP cast iron vacuum pump housing and scroll.

D. Three (3) year warranty from date of final acceptance of all other components including electrical.

QUALITY ASSURANCE

A. Approved Manufacturers

Infrared heating system shall be CORAYVAC® Classic SF infrared heaters as manufactured by Roberts-Gordon LLC, Buffalo, New York.

B. Manufacturer's Qualifications

Firms regularly engaged in manufacture of gas fired infrared systems with characteristics, sizes, and capacities required, whose products have been in satisfactory use in similar service for not less than 15 years.

C. Alternate Manufacturers

1. Other low intensity infrared heaters of equal or greater thermal efficiency and with the same or lower burner firing rate capacity and with the infrared distribution pattern shown on drawing while CSA certified to be in compliance with NFPA 30A 7.6.6 (2012 edition) may be acceptable provided they meet the intent of these specifications and prior approval in writing is obtained from the engineer at least twenty (20) days before the bid date.  If such systems are approved, the contractor assumes responsibility for the design, performance and expense of same.  The redesigned system, gas piping, and electric wiring shall be done by a registered mechanical engineer.  Shop drawings of the entire new system shall be provided by this contractor.  The contractor should state the amount to be credited to the owner due to this substitution.

2. Where approved substitutes are used, the contractor assumes all responsibility for physical dimensions and all other resulting changes.  This responsibility extends to cover all extra work as necessitated by other trades as a result of the substitutions.

3. The engineer reserves the right to require the contractor to remove and replace any material or equipment which does not meet specifications or does not have any prior approval as a substitute item.  Work shall be completed immediately without cost or inconvenience to the owner.

PERFORMANCE SCHEDULE

A. Equipment

- Provide gas fired infrared heaters to deliver the following performance capacities.

Radiant Tube Length 	Radiant Tube Length

Between Burners	Between Burners

Manufacturer	Model	Input Btu/h	Minimum	Maximum

Roberts-Gordon	CRVSF-2	 20,000	   *	21'

Roberts-Gordon	CRVSF-4	 40,000	   *	31' 6”

Roberts-Gordon	CRVSF-6	 60,000	   *	42'

Roberts-Gordon	CRVSF-8	 80,000	   *	52’ 6”

* Refer to manufacture radiant system design manual