VANTAGE® CTHN INFRARED RADIANT HEATERS

PRODUCT SPECIFICATIONS

SYSTEM

- General

1. Mechanical General Requirements

Codes and Standards

1. American National Standard / CSA Standard Gas-Fired Low Intensity Infrared Heaters: Construct and certify gas-fired infrared heaters in accordance with latest edition ANSI Z83.20 / CSA 2.34 "Gas-Fired Low-Intensity Infrared Heaters" including all current supplements.

2. Installation Compliance: United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 - latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 - latest revision.

3. CSA Compliance: Provide CSA Seal affixed to each burner name plate and provide CSA Certification of heater design as vented or unvented infrared heater for indoor installation.

4. National Standard Gas Piping Compliance: Install and connect gas piping to gas fired infrared heaters in accordance with United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 - latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 - latest revision.

5. National Electrical Code Compliance: Install and connect electrical wiring to gas fired infrared heaters in accordance with: 1.) United States: Refer to National Electrical Code®, NFPA 70 - latest revision. Wiring must conform to the most current National Electrical Code®, local ordinances and any special diagrams furnished. 2.) Canada: Refer to Canadian Electrical Code, CSA C22.1 Part 1 - latest revision.

6. National Performance Rating for Gas Fired Infrared Heaters Standard: Radiant output of gas fired infrared heaters shall be rated in accordance with AHRI Standard 1330.  Refer to Performance Rating for Radiant Output of Gas Fired Infrared Heaters Standard CAN/ANSI/AHRI 1330-2015.

EQUIPMENT

A. Burner Box

1. (Natural Gas) (Propane) model, enclosed and sealed box design with silicone gasketed doors and nickel plated steel burner cup, outside air adapter, direct spark ignition, three-try ignition, door interlock safety switch, all components easily accessed, durable spot welded construction, mica flame observation window, balanced air rotor, gas and electric controls are separated from the combustion air stream, and CSA approved.  Burner box paint shall be epoxy-polyester powder coat for corrosion resistance.  Stainless steel flexible gas line and high-pressure gas cock assembly included.

B. Burner Controls

- Factory Wired: All burners shall be factory wired for 120 Vac operation, fully automatic, three-try, direct spark with 100% shut-off electronic ignition control.

2.	Fail-Safe Controls: To assure a high degree of fail-safe operation, the design shall preclude main flow of gas 	if any or all of the following abnormal conditions occur:

a. Power fails (Gas valves in burners close in safe position).

b. Vacuum pump motor fails (Vacuum proving switch cuts power to burners).

3. Ignition Controls: All gas vacuum-firing burner units shall be equipped with a Direct Spark Ignition Module (DSI).  The DSI module shall have a 15-second flame response time per ignition trial before lockout occurs.  In addition, the DSI module shall be capable of a minimum of 3 trials for ignition to provide maximum reliability.

- Motor/Blower Assembly for Unitary Heaters

1. Motor 120V, balanced air rotor. Motor shall be equipped with permanently lubricated ball bearings. Motor shall be equipped with thermal overload protection.

2.	Motor/blower assembly to be attached to end of heat exchanger using fan flange, to create a negative pressure system.

D. Vacuum Pump For Multiburner System

1. Outdoor Venting: The system shall vent all products of combustion outdoors by means of the vacuum pump.

2. Motor: Vacuum pump shall be equipped with a maximum of 3/4 horsepower, 60 Hz, 115 Vac, 3450 RPM, single phase motor.  This motor shall have thermal overload protection, ball bearings, and shall be constructed in accordance with electric motor industry standards.

3. Housing: The scroll shall be cast iron with a minimum metal thickness of approximately 3/16 inch. The impeller wheel shall be cast 319 alloy aluminium with a minimum metal thickness of approximately 3/32 inch.

4. Vacuum Proving Switch: Low voltage, 24 V, two wire interlock circuit from the vacuum proving switch (located at the inlet to the vacuum pump) to the control panel.

5. High Temperature Acoustic Boots: The connection between the pump inlet and manifold pipe is made with acoustic boot and steel tube.

6. Rotation: Vacuum pump motor requires 115 V, single phase, 60 Hz for a maximum of 10 full load amps. Pump rotation is field selectable depending installation configuration.

7. Acoustic Isolation: The vacuum pump shall be acoustically isolated from the system with a flexible connector with a constant service temperature rating of 350F minimum. The motor in the vacuum pump shall be secured with rubber mounts for acoustical isolation.

E. Reflectors

Provide high radiant reflective aluminum reflectors installed over all heat exchanger tube.  Provide wide parabolic design reflector with 12 reflective surfaces that when tested with select models* can enhance model to an Infrared Factor (IF) of 15 when tested in accordance to AHRI standard 1330 (latest edition) for Radiant Output of Gas Fired Infrared Heaters.  Reflector shall reflect 100% of the infrared energy that it receives from the heat exchanger tube directly to the floor.  Reflectors with less than 12 reflective surfaces shall not be allowed.  In order to maximize radiant output and reduce convective heat losses, reflectors are to extend below the bottom of the heat exchanger tube.  Provide continuous reflector over all tube and fitting heat exchanger surfaces.  Provide reflector end caps as necessary to reduce convective heat losses.

*Multiple models rated in accordance with AHRI Standard 1330 have achieved an Infrared Factor (IF) of 15, models included: CTH2-100 @ 30’ tested with straight orientation, HRS & HT Aluminized tubing with high efficiency reflector.

E.  Reflectors - Standard

Provide high radiant reflective (aluminum) (stainless steel) reflectors installed over all heat exchangers.  Provide reflector joint pieces over heat exchanger fittings such as elbows so reflector covers heat exchanger continuously.  In order to maximize radiant output and reduce convective heat losses, reflectors are to extend below the bottom of the heat exchanger tube.

1. Over all fittings: All reflectors at termination of the heat exchanger pipe and any elbows shall have end caps to prevent convective heat from escaping.

2. Side Reflectors: System to have (aluminum) (stainless steel) perimeter side extension reflector in certain areas of layout as shown on plan where specified.  Side reflectors permanently attach to side to top reflector and are secured to the pipe by side reflector supports and two "Z" clips for each 8’ (2.44 m) section of side reflector.  To prevent convection losses, tilting of reflectors will not be acceptable.

F. Outside Air

Provide fresh outside air to supply each burner for the support of combustion air.

G. Controls

- Thermostats: Provide where indicated, line voltage or low voltage type connected to infrared heater. Mount thermostat 5ft. – 6 ft. above finish floor or as otherwise noted on the drawing. All thermostats shall be numbered instead of marked in degrees and shall not have thermometers.

- ROBERTS GORDON® CORAYVAC® Heating Control (for use with multiburner system only): Provide where indicated, a single control panel capable of managing four zones of burners’ temperature control and power. The control will also give power output to as many as two pumps, provided that the load is not greater than 20 A and 1 Ø.  The control panel shall have indicator lights showing: Line Power, Pump 1 Power, Pump 2 Power, Pressure Switch 1 Power, Pressure Switch 2 power and 4-Zones. The panel shall include a 24 VAC power supply to supply power to electronic thermostats and shall be capable of using mechanical thermostats equipped with a heat anticipator.  The control panel enclosure shall be painted steel and shall include indicator lights to display when line power is available to the panel, when the vacuum pumps are energized, when the vacuum proving switches are closed and when the burner zone relays are energized.  The control panel shall have separate line voltage and low voltage terminal strips for ease of wiring.  The control panel shall be manufactured by the same manufacture as the infrared burners and vacuum pumps for single-source accountability.

H. Infrared Piping - Heat Exchanger

- Infrared Tube shall be new 4 in. O.D. (Heat Treated Aluminized) (Hot-Rolled) steel tube X 16 gauge wall with an emissivity factor of 0.80 or greater.

- Burner Tube: shall be ALUMITHERM® steel (aluminized steel/titanium alloy) tube for the first 10 ft. of each infrared heater.

- Fittings for infrared tube shall be as described in the installation manual.

- Hanging Materials: All system’s tube must be supported in accordance with acceptable practices, local codes, seismic requirements, and applicable standards and as shown on plans.

I. Manifold Piping for Muiltiburner Systems

1.	Manifold Tube shall be new 4 in. Heat Treated Aluminized tubing X 16 gauge wall.

2.	Fittings for manifold piping shall be as described in the installation manual.

3.	Hanging Materials: All systems pipe must be supported in accordance with acceptable practices, local codes, seismic requirements, applicable standards and as shown on plans. Manifold piping shall pitch at least 1/2 inch in 20 feet, away from burner.

INSTALLATION OF GAS FIRED INFRARED HEATERS

A. General

Install gas fired infrared heaters as indicated, in accordance with manufacturer's installation instructions and in compliance with applicable codes and approvals.  Allow adequate space for servicing or removal of the unit without disturbing other piping or equipment.

B. Support

Suspend heat exchanger, burner, gas piping, conduit, and reflectors from building substrate as indicated, or if not indicated, in manner to provide durable and safe installation; and in accordance with manufacturer's installation instructions.  Mounting height to be a minimum         feet from floor level.

C. Clearance to Combustibles

Do not exceed clearance to combustibles outlined and printed on burner nameplate, and in manufacturer's product data.  Measure clearance distance from surface of heat exchanger or as indicated by approval agency's listing.

D. Venting

Install vent piping as indicated.  Terminate where indicated on the drawings with a vent terminal assembly as supplied by the manufacturer.

E. Gas Piping

Install gas piping as indicated and in accordance with Z233.1 National Fuel Gas Code installation codes (latest edition).

- Required Gas Supply Inlet Pressures:

# Natural Gas Units		Required Minimum Gas Pressure	Maximum Gas Pressure

40,000-150,000 Btu/h		4.6” wc			14” wc

175,000 Btu/h -200,000 Btu/h	5.0” wc			14” wc

# Propane Gas Units		Required Minimum Gas Pressure	Maximum Gas Pressure

40,000-200,000 Btu/h		11.0” wc		14” wc

- Local Codes: Gas supply piping must meet local requirements and be sized in accordance with Btu/h demand, available pressure and total length of supply line required for the installation.  Connection from supply line to burner unit must be made in accordance with installation instructions.  Gas shut-off cock, as supplied with unit, and controls in unit must not be subjected to more than 1/2 lb. or 14 in. wc pressure.

- Drip Legs: Provide drip legs at all gas risers.

F. Electrical Wiring

Install electrical wiring as indicated.  Connect power wiring to burners and control wiring between burners and thermostats in accordance with manufacturer's wiring diagrams.

FIELD QUALITY CONTROL

A. Start-Up

Start-up, test, and adjust gas fired infrared heaters in accordance with manufacturer's start-up instructions, and Utility Company's requirements.  Check and calibrate controls, adjust burners if applicable according to manufacturer's instructions for maximum efficiency.

CLOSEOUT PROCEDURES

A. Training

Provide services of manufacturer's technical representative to instruct operating personnel in operation and maintenance of gas fired infrared heaters.

1. Schedule instruction with operating building owner, provide at least 7 days notice.

WARRANTY

Provide written warranty, by manufacturer, agreeing to replace/repair, within warranty period, components of gas fired infrared systems furnished by manufacturer, which are defective in either material or workmanship, provided manufacturer's instructions for handling, installing, protecting, and maintaining units have been adhered to during warranty periods follows:

A. Three (3) year warranty on the burner system and on the tubing from date of final acceptance of the infrared 	heaters.

B. Three (3) from date of final acceptance of all other components including electrical.

QUALITY ASSURANCE

A. Approved Manufacturers

Infrared heating system shall be VANTAGE® NP infrared heaters as manufactured by Roberts-Gordon Inc., Buffalo, New York.

B. Manufacturer's Qualifications

Firms regularly engaged in manufacture of gas fired infrared systems with characteristics, sizes, and capacities required, whose products have been in satisfactory use in similar service for not less than 15 years.

C. Alternate Manufacturers

1. Other low intensity infrared heaters of equal or greater thermal efficiency and with the same or lower burner firing rate capacity, and with the infrared distribution pattern shown on drawing may be acceptable provided they meet the intent of these specifications and prior approval in writing is obtained from the engineer at least twenty (20) days before the bid date.  If such systems are approved, the contractor assumes responsibility for the design, performance and expense of same.  The redesigned system, gas piping, and electric wiring shall be done by a registered mechanical engineer.  Shop drawings of the entire new system shall be provided by this contractor.  The contractor should state the amount to be credited to the owner due to this substitution.

2. Where approved substitutes are used, the contractor assumes all responsibility for physical dimensions and all other resulting changes.  This responsibility extends to cover all extra work as necessitated by other trades as a result of the substitutions.

3. The engineer reserves the right to require the contractor to remove and replace any material or equipment which does not meet specifications or does not have any prior approval as a substitute item.  Work shall be completed immediately without cost or inconvenience to the owner.

PERFORMANCE SCHEDULE

A. Equipment

- Provide gas fired infrared heaters to deliver the following performance capacities.

Manufacturer	 Model	Input	Overall Length 	Overall Length

Btu/h	Minimum             	 Maximum

Roberts-Gordon	CTHN-40	 40,000	   12' 3"	12' 3"

Roberts-Gordon	CTHN-60	 60,000	   22' 3"	22' 3"

Roberts-Gordon	CTHN-80	 80,000	   22' 3" 	22' 3"

Roberts-Gordon	CTHN-100	100,000	   32' 3"	32' 3"

Roberts-Gordon	CTHN-125	125,000	   42' 3"	42' 3"

Roberts-Gordon	CTHN-150	150,000	   42' 3"	42' 3"

Roberts-Gordon	CTHN-175 	175,000	   52' 3"	52' 3"

Roberts-Gordon	CTHN-200	200,000	   52' 3"	52' 3"