CORAYVAC® WITH CORAYVAC® MODULATING HEATING CONTROLS INFRARED RADIANT HEATERS

PRODUCT SPECIFICATIONS

SYSTEM

- General

1. Condensing System:  Design gas-fired radiant systems to operate such that water vapor present in products of combustion will be condensed, and this heat of condensation will be extracted by the system and will be added to the heated space.

2. Vacuum Vented:  To preclude the possibility of combustion gases escaping into the building, the entire system must be under a negative pressure at all times and vacuum vented to the outside atmosphere.

- Codes and Standards

1. American National Standard / CSA Standard Gas-Fired Low Intensity Infrared Heaters: Construct and certify gas-fired infrared heaters in accordance with latest edition ANSI Z83.20 / CSA 2.34 "Gas-Fired Low-Intensity Infrared Heaters" including all current supplements.

2. Installation Compliance: United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 - latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 - latest revision.

3. CSA Compliance: Provide CSA Seal affixed to each burner name plate and provide CSA Certification of heater design as vented or unvented infrared heater for indoor installation.

4. National Standard Gas Piping Compliance: Install and connect gas piping to gas fired infrared heaters in accordance with United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 - latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 - latest revision.

5. National Electrical Code Compliance: Install and connect electrical wiring to gas fired infrared heaters in accordance with: 1.) United States: Refer to National Electrical Code®, NFPA 70 - latest revision. Wiring must conform to the most current National Electrical Code®, local ordinances and any special diagrams furnished. 2.) Canada: Refer to Canadian Electrical Code, CSA C22.1 Part 1 - latest revision.

6. National Performance Rating for Gas Fired Infrared Heaters Standard: Radiant output of gas fired infrared heaters shall be rated in accordance with AHRI Standard 1330.  Refer to Performance Rating for Radiant Output of Gas Fired Infrared Heaters Standard CAN/ANSI/AHRI 1330-2015.

EQUIPMENT

A. Burner Box

1. (Natural Gas) (Propane) model, burner assemblies consisting of heavy duty cast iron burner heads, other substitutions will not be accepted. Pre-wired gas controls with direct spark ignition module, and combustion air filters supplied. Provide minimum numbers of burners indicated to insure proper radiant heat distribution.  Fewer burners of larger capacity will not be accepted. Burners shall be designed for firing in tandem without adverse effects from combustion gases from upstream burners.

2. Design firing rate of burners shall be XXXXXXX Btu's per hour as stated on drawings. Clearances to a combustibles surface as measured from the tube surface shall not exceed XX" above, XX" below, XX" on each side.

3. Premix Gas and Air:  Provide burners to totally pre-mix air and gas required for combustion.

4. Constant Air/Gas Ratio:  Provide burners designed to maintain constant proportion of fuel gas to filtered combustion air. Introduce both fuel gas and air at atmospheric pressure, and establish flow of both by means of negative pressure on the downstream side of the flow metering orifices.  Design so that if combustion air flow is impeded for any reason, gas flow rate will decrease in constant proportion to maintain proper gas/air mixture for complete combustion.

B. Burner Controls

- Factory Wired: All burners shall be factory wired for 115 VAC with transformer for 24 VAC DSI operation and supplied with a grounded 24-30 inch (61–76 cm) three wire pigtail located at rear of burner

2.	Fail-Safe Controls: To assure a high degree of fail-safe operation, the design shall preclude main flow of gas 	if any or all of the following abnormal conditions occur:

a. Power fails (Gas valves in burners close in safe position).

b. Main Valve fails in open position

c. Vacuum pump motor fails (Vacuum proving switch cuts power to burners).

3. Ignition Controls: All gas vacuum-firing burner units shall be equipped with a Direct Spark Ignition Module (DSI).  The DSI module shall have a 15-second flame safety time per ignition trial before lockout occurs.  In addition, the DSI module shall be capable of a minimum of 3 trials for ignition to provide maximum reliability.

C. Vacuum Pump

Vacuum Pump 1/3 HP Option:

  - Outdoor Venting:  The system shall vent all products of combustion outdoors by means of the vacuum pump.

  - Motor:  Vacuum pump shall be equipped with a 1/3 horsepower, 60 hertz, 120/230 volts AC, 3450 RPM, single phase motor.  This motor shall have thermal overload protection, high temperature sealed ball bearings, and shall be constructed in accordance with electric motor industry standards.

  - Housing:  The scroll of this pump shall 12-gauge stamped steel construction.  The impeller wheel shall be pressure cast 319-alloy aluminum with a minimum metal thickness of approximately 3/32 inch (.24 cm).

  - Pressure Switch:  As an additional safety measure, there will be a low voltage (24 VAC) interlock circuit from the pressure switch (located at the inlet to the vacuum pump) to the controller to prove pump operation.

  - High Temperature Acoustical Isolation:  The vacuum pump shall be acoustically isolated from the system with a flexible connector with a constant service temperature rating of 350ºF (177°C) minimum.  The connection between the 4” (10 cm) pump inlet and tailpipe is made with acoustic boot and clamps provided.  The discharge connection is made with an acoustic boot and schedule 40 steel pipe or 4 inch (10 cm) ABS schedule 5 pipe and fittings.  The motor in the vacuum pump shall be secured with rubber mounts for acoustical isolation.

  - Rotation:  Vacuum pump motor requires a grounded circuit 120/230 volts AC, single phase, 60 hertz for a maximum of 4.8/2.4 full load.  This motor must have the same rotation to match the direction of the arrow on the fan scroll.  If the motor is not rotating in this direction, it must be reversed by interchanging the black and red line leads as shown on the motor nameplate.

Vacuum Pump 3/4 HP Option:

- Outdoor Venting:  The system shall vent all products of combustion outdoors by means of the vacuum pump.

- Motor:  Vacuum pump shall be equipped with a 3/4 horsepower, 60 hertz, 208-230/460 volts AC, 3450 RPM, three phase motor.  This motor shall have thermal overload protection, high temperature sealed ball bearings, and shall be constructed in accordance with electric motor industry standards.

- Motor:  Vacuum pump shall be equipped with a 3/4 horsepower, 60 hertz, 120/230 volts AC, 3450 RPM, single phase motor.  This motor shall have thermal overload protection, high temperature sealed ball bearings, and shall be constructed in accordance with electric motor industry standards.

- Housing:  The scroll of this pump shall be cast iron with a minimum metal thickness of approximately 3/16 inch (.48 cm).  The impeller wheel shall be pressure cast 319-alloy aluminum with a minimum metal thickness of approximately 3/32 inch (.24 cm).

- Pressure Switch:  As an additional safety measure, there will be a low voltage (24 VAC) interlock circuit from the pressure switch (located at the inlet to the vacuum pump) to the controller to prove pump operation.

- High Temperature Acoustical Isolation:  The vacuum pump shall be acoustically isolated from the system with a flexible connector with a constant service temperature rating of 350ºF (177°C) minimum.  The connection between the 4.5” (11 cm) pump inlet and tailpipe is made with acoustic boot and clamps provided.  The discharge connection is made with an acoustic boot and schedule 40 steel pipe or 4 inch (10 cm) ABS schedule 5 pipe and fittings.  The motor in the vacuum pump shall be secured with rubber mounts for acoustical isolation.

- Rotation:  Vacuum pump motor requires a grounded circuit 208-230/460 volts AC, three phase, 60 hertz for a maximum of 2.5 full load amps via a variable frequency drive.  This motor must have the same rotation to match the direction of the arrow on the fan scroll.  If the motor is not rotating in this direction, it must be reversed by interchanging any 2 line leads as indicated on the motor nameplate.

- Rotation:  Vacuum pump motor requires a grounded circuit 120/230 volts AC, single phase, 60 hertz for a maximum of 6.6 full load amps.  This motor must have the same rotation to match the direction of the arrow on the fan scroll.  If the motor is not rotating in this direction, it must be reversed by interchanging the black and red line leads as indicated on the motor nameplate.

- Speed Control:  Vacuum pump motor speed and power supply shall be from a 3/4 HP (208-230/460V) three phase or 1HP (120/230VAC) single phase variable frequency drive.   Variable frequency drive power input shall be specified as either 120/230VAC, 1 ph, 60 Hz, 16.6A; or 208-230/460V, 3 ph, 60 Hz, 6.9A.  Variable frequency drive output frequency shall control the speed of the vacuum pump motor by speed reference following analog signal.

Vacuum Pump 2 HP Option:

- Outdoor Venting:  The system shall vent all products of combustion outdoors by means of the vacuum pump.

- Motor:  Vacuum pump shall be equipped with a 2 horsepower, 60 hertz, 208-230/460 volts AC, 3450 RPM, three phase motor.  This motor shall have thermal overload protection, high temperature sealed ball bearings, and shall be constructed in accordance with electric motor industry standards.

- Motor:  Vacuum pump shall be equipped with a 2 horsepower, 60 hertz, 208-230 volts AC, 3450 RPM, single phase motor.  This motor shall have thermal overload protection, high temperature sealed ball bearings, and shall be constructed in accordance with electric motor industry standards.

- Housing:  The scroll and impeller wheel of this pump shall be 3 mm welded steel construction.

- Pressure Switch:  As an additional safety measure, there will be a low voltage (24 VAC) interlock circuit from the pressure switch (located at the inlet to the vacuum pump) to the controller to prove pump operation.

- High Temperature Acoustical Isolation:  The vacuum pump shall be acoustically isolated from the system with a flexible connector with a constant service temperature rating of 350ºF (177°C) minimum.  The connection between the 6” (15 cm) pump inlet and tailpipe is made with acoustic boot and clamps provided.  The discharge connection is made with an acoustic boot and 6” (15 cm) pipe and fittings.

- Rotation:  Vacuum pump motor requires a grounded circuit 208-230/460 volts AC, three phase, 60 hertz for a maximum of 5.5 full load amps via a variable frequency drive.  This motor must have the same rotation to match the direction of the arrow on the fan scroll.  If the motor is not rotating in this direction, it must be reversed by interchanging any 2 line leads as shown on the motor nameplate.

- Rotation:  Vacuum pump motor requires a grounded circuit 208-230 volts AC, single phase, 60 hertz for a maximum of 12.8 full load amps.  This motor must have the same rotation to match the direction of the arrow on the fan scroll.  If the motor is not rotating in this direction, it must be reversed by interchanging the specified line leads as shown on the motor nameplate.

E. Reflectors – High Efficiency

Provide high radiant reflective aluminum reflectors installed over all heat exchanger tube.  Provide wide parabolic design reflector with 12 reflective surfaces that when tested with select models* can enhance model to an Infrared Factor (IF) of 15 when tested in accordance to AHRI standard 1330 (latest edition) for Radiant Output of Gas Fired Infrared Heaters.  Reflector shall reflect 100% of the infrared energy that it receives from the heat exchanger tube directly to the floor.  Reflectors with less than 12 reflective surfaces shall not be allowed.  In order to maximize radiant output and reduce convective heat losses, reflectors are to extend below the bottom of the heat exchanger tube.  Provide continuous reflector over all tube and fitting heat exchanger surfaces.  Provide reflector end caps as necessary to reduce convective heat losses.

*Multiple models rated in accordance with AHRI Standard 1330 have achieved an Infrared Factor (IF) of 15, models included: CTH2-100 @ 30’ tested at horizontal orientation with high efficiency reflector.

C.  Reflectors - Standard

Provide high radiant reflective (aluminum) (stainless steel) reflectors installed over all heat exchangers.  Provide reflector joint pieces over heat exchanger fittings such as elbows so reflector covers heat exchanger continuously.  In order to maximize radiant output and reduce convective heat losses, reflectors are to extend below the bottom of the heat exchanger tube.

1. Over all fittings: All reflectors at termination of the heat exchanger pipe and any elbows shall have end caps to prevent convective heat from escaping.

2. Side Reflectors: System to have (aluminum) (stainless steel) perimeter side extension reflector in certain areas of layout as shown on plan where specified.  Side reflectors permanently attach to side to top reflector and are secured to the pipe by side reflector supports and two "Z" clips for each 8’ (2.44 m) section of side reflector.  To prevent convection losses, tilting of reflectors will not be acceptable.

3. Over Entire pipe Network: Reflectors shall be installed on all radiant pipe and tail pipe as indicated on system layout                  furnished.

F. Outside Air

Provide fresh outside air to supply each burner and end vent for the support of combustion air as called for on plans.  Fresh outside air supply must be installed in accordance with the requirements within the installation operation and service manual.

- Outside Air Blower: Blower shall be 167 watt, 60 hertz, 120 volts AC, 3000 RPM, single phase motor.  Provides system with pressured outside air supply to each burner and end vent for the support of combustion air as called for on plans.

G. Controls

- ROBERTS GORDON® CORAYVAC® Modulating Heating Control: The control of the radiant heating system shall be via ROBERTS GORDON® CORAYVAC® Modulating Heating Control.  The ROBERTS GORDON® CORAYVAC® Modulating Heating Control shall provide for modulation of the CORAYVAC® system firing rate based on outdoor air temperature.  At external design temperature conditions, the system shall provide 100% input.  At conditions milder than external design temperatures, the system shall modulate input continuously (not staged) between 60% and 100% input. The ROBERTS GORDON® CORAYVAC® Modulating Heating Control shall incorporate the following features:

- Codes and Standards:

- Energy Management Equipment: Construct and certify energy management controller in accordance with the latest edition of the United States standard UL916 and Canadian Standard C22.2 No. 205-M1983 including all current supplements.

- ASHRAE standard 90.1 Energy Efficient Design of New Buildings Except Low-Rise Residential Buildings: In accordance with 6.2.3.2, HVAC systems having a design heating capacity greater than 65,000 Btu/h and fan system power greater than ¾ hp shall have all the following off-hour controls: Automatic shutdown (6.2.3.2.1), Setback controls (6.2.3.2.2).

c.	Electrical installation codes of practice:  All control and line voltage external wiring to be undertaken in accordance with the latest edition of the National Electric Code.

- Controller Construction:

  - Enclosure manufactured in 14 Gauge Steel, NEMA Type 1 enclosure with hinged door for ease of maintenance.

  - Microprocessor based controller with pre-configured touchscreen programming. Utilizing control mounted touchscreen interface for entry and access of all stored information.

  - High visibility power indicator lights: Input power, four (4) Zone power and two (2) Vacuum Pump power.

  - Four digital switching relays, affording up to four heating zones.

  - Twelve universal inputs. The function of the inputs is for safety switches, zone occupancy override signals, indoor and outdoor air temperature inputs, local zone temperature setpoint adjustment signals, and building management system enable/disable signal.

  - MODBUS® output signal for control of variable frequency drive.

  - BACnet® MS/TP for inter-panel communication.

  - Proprietary Rnet communication for zone sensors.

  - Eight universal outputs, four for zone ON/OFF control, four for modulation signal to unitary burners.

- General Specification:

- ROBERTS GORDON® CORAYVAC® Modulating Heating Control:  Radiant heater controller shall provide zone temperature, outdoor temperature and system monitoring features viewed and altered via touchscreen controls, heater power supply output and speed signal output for variation of vacuum pump speed.

- Variable Frequency Drive/Modulation:  System shall modulate by adjusting the vacuum pressure via variable frequency drive based on speed referenced from controller, not motorized damper control.

- Zone Time and Temperature Facilities:

For each heated zone, the following automatic shutdown and set back control functions shall be provided:

a.	Status display indicating the following:

i.	Current Sensed Zone Temperatures

- Setpoint Temperatures

- Setback Setpoint Temperature

- Current Setpoint Adjustment Value

- Heat Power ON/OFF Indication (for each individual zone)

- Pump Power ON/OFF Indication

- Pump Speed

- Outdoor Air Temperature

c.	Manual timed override of heating from setback to occupied condition shall be provided on each zone sensor.  Timed period shall be customized for each zone at the sensor or touchscreen controls.

d.	Manual setpoint temperature lower and upper offset adjustment shall be provided on each zone sensor.  Adjustment range shall be specified via touchscreen controls.

- Diagnostics: The control shall provide the ability to view the following information at the touchscreen display.

  - Display of up to a 7-day history of hours run data for each individual heated zone.  History period and data logging frequency available in 15 minute intervals.

  - Display up to a 7-day history of temperatures sensed data for each individual heated zone. History period and data logging frequency available in 15 minute intervals.

  - An input reserved for remote enable. The input is suitable for connection through normally open contacts provided by a remote switch, such that upon activation of the remote switch, the CORAYVAC® Modulating Heating Control will maintain the OCCUPIED temperature setting. Upon deactivation of the remote switch, the CORAYVAC® Modulating Heating Control will maintain the SETBACK temperature setting.  Remote enable status shall be monitored from touchscreen.

  - Safety of the pressure switch proving circuit shall be maintained by the circuit being proved in the normally open position prior to the vacuum pump being energized. The pressure switch will then be proved in the normally closed position once the required system pressure has been established.  Pressure switch position shall be monitored via touchscreen.

- External Wiring

- The network shall be BACnet® MS/TP RS-485 communication bus. Wiring to be in 22AWG shielded cable. Supplied by others.

- The network shall be a daisy chain where the bus must form a single continuous path.

- The temperature in each zone shall be sensed by a multi-featured electronic air sensor. Wiring to be four-wire 22AWG shielded cable. Supplied by others.

- The power supply to the control panel shall be 120V, 1 phase 60Hz and shall be taken from a suitably protected circuit supplied by others.  A separate power supply is required for variable frequency drive(s).  Refer to manufacture installation, operation and service manual.

- Any vacuum pumps used in conjunction with Roberts-Gordon equipment shall have their own power supply rated for the applicable current load through a variable frequency drive supplied by Roberts-Gordon.  Power supply to the variable frequency drive must be either 115V 1 ph 60Hz, 230V 1ph 60Hz, 230V 3ph 60Hz, or 460V 3ph 60Hz per variable frequency drive specification.

- The output to each zone shall be 120 Volts, 1 phase 60Hz. The zone current requirements must not exceed 5.0 Amps.

- The maximum supply to the controller shall be 20 Amps at 120Volts, 1 phase 60Hz.

- Local and Remote Communications

- Local Communications: One controller in network shall be noted as “Central Controller”.  Remaining controllers shall be noted as “Satellite Controllers”.  Central controller in network shall have touchscreen controls to provide for local direct communication to satellite controllers via RS-485 wiring.  A ‘Repeater’ (provided by Roberts-Gordon) shall be required if RS-485 wiring between controllers exceeds 4000’ (1,219 m) as stated in manufacture installation, operation and service manual.

- Remote Communications: One controller in the network shall have either item i., or i and ii (supplied by Roberts-Gordon) and will be noted as “Central Controller”.  Remaining controllers in the network shall be noted as “Satellite Controllers”.

    - Touchscreen located on central controller for connection to satellite controllers to allow on-site communications to all CORAYVAC® Modulating Heating Controls via network communications bus between controllers in the network via RS-485 wiring as stated in manufacture installation, operation and service manual.

    - WebCTRL® automation system interface through (HTTP) to communicate over the internet or intranet shall allow remote, off-site direct communication to central controller.  Allow complete access to all touchscreen features through WebCTRL® that include but not limited to:

- Setting and changing schedules

- Adjust setpoints and other control properties

- Graphically trending important building conditions

- Viewing and acknowledging alarms

- Custom alarm management capabilities to allow notifications via e-mail, text messaging, etc. for situations such as when zone temperatures drop below setpoints, or exceed user-defined requirements.

- Thermostats: Provide where indicated, line voltage or low voltage type connected to infrared heater. Mount thermostat 5’ – 6’ (1-2 m) above finish floor or as otherwise noted on the drawing. All thermostats shall be numbered instead of marked in degrees and shall not have thermometers.

- ROBERTS GORDON® CORAYVAC® Heating Control: Provide where indicated, a single control panel capable of managing four zones of burners’ temperature control and power. The control will also give power output to as many as two pumps, provided that the load is not greater than 20 A and 1 Ø.  The control panel shall have indicator lights showing: Line Power, Pump 1 Power, Pump 2 Power, Pressure Switch 1 Power, Pressure Switch 2 power and 4-Zones. The panel shall include a 24 VAC power supply to supply power to electronic thermostats and shall be capable of using mechanical thermostats equipped with a heat anticipator.  The control panel enclosure shall be painted steel and shall include indicator lights to display when line power is available to the panel, when the vacuum pumps are energized, when the vacuum proving switches are closed and when the burner zone relays are energized.  The control panel shall have separate line voltage and low voltage terminal strips for ease of wiring.  The control panel shall be manufactured by the same manufacture as the infrared burners and vacuum pumps for single-source accountability.

H. Infrared Piping – Radiant Piping - Heat Exchanger

- Radiant Tube: Shall be new 4 in. (10 cm) O.D. (Heat Treated Aluminized) (Hot-Rolled) (Porcelain Coated) steel tube X 16 gauge wall with an emissivity factor of 0.80 or greater.

- Tail Pipe Tube: Shall be new 4 in. (10 cm) O.D. (Heat Treated Aluminized) (Porcelain Coated) steel tube X 16 gauge wall with an emissivity factor of 0.80 or greater.

- Fittings: Shall be 4 in. (10 cm) O.D. (Aluminized) (Porcelain Coated) steel X 16 gauge wall. For tubes shall be as described in the installation, operation and service manual.

- Hanging Materials: All system’s tube must be supported in accordance with acceptable practices, local codes, seismic requirements, and applicable standards and as shown on plans. Pipe shall pitch down at least ½” in 20’ (1.27 cm in 6.1 m) on radiant lines and 1” in 20’ (1.27 cm in 6.1 m) on tailpipe lines toward the vacuum pump.

- End Vent Assembly: Each open end combustion chamber shall have an approved end vent and the reflector shall terminate with an end cap, and be installed according to manufacturer’s installation operation and service manual and as shown on plans.

- Condensate Piping: Above Ground:  copper tubing type M hard drawn. Fittings: ANSI/ASME 816.23 cast brass or ANSI/AMSE 816.29, wrought copper.  Joints ANSI/ASTM B32, solder, grade 95TA.

- Condensate Neutralization Tube: Provide and install condensate neutralization tube as per the manufacture instructions in the installation operation and service manual.

INSTALLATION OF GAS FIRED INFRARED HEATERS

A. General

Install gas fired infrared heaters as indicated, in accordance with manufacturer's installation operation and service manual and in compliance with applicable codes and approvals.  Allow adequate space for servicing or removal of the unit without disturbing other piping or equipment.

B. Support

Suspend heat exchanger, burner, gas piping, conduit, and reflectors from building substrate as indicated, or if not indicated, in manner to provide durable and safe installation; and in accordance with manufacturer's installation operation and service manual.  Mounting height to be a minimum         feet (_____ m) from floor level.

C. Clearances to Combustibles

Always maintain clearance to combustibles as outlined and printed on burner nameplate and in manufacturer's product data.  Measure clearance distance from surface of heat exchanger or as indicated by approval agency's listing.

D. Venting

Install vent piping as indicated on plans.  Terminate where indicated on the drawings with a vent terminal assembly as supplied by the manufacturer. The venting must be installed in accordance with the requirements within the installation operation and service manual and the following codes: United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 - latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 - latest revision.

E. Gas Piping

Install gas piping as indicated and in accordance and in compliance with applicable codes and approval: United States: Refer to National Fuel Gas Code NFPA 54/ANSI Z223.1 - latest revision. Canada: Refer to Natural Gas and Propane Installation Code CSA B149.1 - latest revision.

- Required Gas Supply Inlet Pressures:

# Natural Gas Units	Required Minimum Gas Pressure	Maximum Gas Pressure

20,000-120,000 Btu/h	4.5” wc	14” wc

# Propane Gas Units	Required Minimum Gas Pressure	Maximum Gas Pressure

40,000-110,000 Btu/h	10.5” wc	14” wc

- Local Codes: Gas supply piping must meet local requirements and be sized in accordance with Btu/h demand, available pressure and total length of supply line required for the installation.  Connection from supply line to burner unit must be made in accordance with installation operation and service manual.  Gas shut-off cock, as supplied with unit, and controls in unit must not be subjected to more than 1/2 lb. or 14” wc pressure.

- Drip Legs: Provide drip legs at all gas risers.

F. Electrical Wiring

Install electrical wiring as indicated. Connect power wiring to burners and vacuum pumps, control wiring between burners, vacuum pump, control panels, thermostats, timers, relays, and transformers, in accordance with manufacturer’s wiring diagrams.

G. Thermostats

Provide where indicated, 24VAC thermostat, connected to control system.  Mount thermostat 5’ 6” (1.67 m) above finish floor or otherwise as noted on the drawing. Low voltage thermostats shall be numbered instead of marked in degrees and shall not have thermometers. Low voltage wiring must follow local codes.

FIELD QUALITY CONTROL

A. Start-Up

Start-up, test, and adjust gas fired infrared heaters in accordance with manufacturer's start-up instructions in the installation operation and service manual, and Utility Company's requirements.  Check and calibrate controls, adjust burners if applicable according to manufacturer's installation operation and service manual instructions for maximum efficiency.

CLOSEOUT PROCEDURES

A. Training

Provide services of manufacturer's technical representative to instruct operating personnel in operation and maintenance of gas fired infrared heaters.

1. Schedule instruction with operating building owner, provide at least 7 days notice.

WARRANTY

Provide written warranty, by manufacturer, agreeing to replace/repair, within warranty period, components of gas fired infrared systems furnished by manufacturer, which are defective in either material or workmanship, provided manufacturer's instructions for handling, installing, protecting, and maintaining units have been adhered to during warranty periods follows:

A. Three (3) year warranty on the burner system from the date of final acceptance of the infrared heaters.
      B. Twenty Five (25) year warranty from the date of final acceptance of 3/4 HP cast iron vacuum pump housing and scroll.

C. Three (3) year warranty from date of final acceptance of all other components including electrical

QUALITY ASSURANCE

A. Approved Manufacturers

Infrared heating system shall be CORAYVAC® infrared heaters as manufactured by Roberts-Gordon LLC, Buffalo, New York.

B. Manufacturer's Qualifications

Firms regularly engaged in manufacture of gas fired infrared systems with characteristics, sizes, and capacities required, whose products have been in satisfactory use in similar service for not less than 15 years.

C. Alternate Manufacturers

1. Other low intensity infrared heaters (of equal or greater thermal efficiency) (of an Infrared Factory (IF) as high as 15 when tested in accordance to AHRI standard 1330 for Radiant Output of Gas Fired Infrared Heaters,) and with the same or lower burner firing rate capacity, and with the infrared distribution pattern shown on drawing may be acceptable provided they meet the intent of these specifications and prior approval in writing is obtained from the engineer at least twenty (20) days before the bid date.  If such systems are approved, the contractor assumes responsibility for the design, performance and expense of same.  The redesigned system, gas piping, and electric wiring shall be done by a registered mechanical engineer.  Shop drawings of the entire new system shall be provided by this contractor.  The contractor should state the amount to be credited to the owner due to this substitution.

2. Where approved substitutes are used, the contractor assumes all responsibility for physical dimensions and all other resulting changes.  This responsibility extends to cover all extra work as necessitated by other trades as a result of the substitutions.

3. The engineer reserves the right to require the contractor to remove and replace any material or equipment which does not meet specifications or does not have any prior approval as a substitute item.  Work shall be completed immediately without cost or inconvenience to the owner.

PERFORMANCE SCHEDULE

A. Equipment

- Provide gas fired infrared heaters to deliver the following performance capacities.

Radiant Tube Length 	Radiant Tube Length

Between Burners	Between Burners

Manufacturer	Model	Input Btu/h	Minimum	Maximum

Roberts-Gordon	B-2	 20,000	   10'	20'

Roberts-Gordon	B-4	 40,000	   12' 6"	25'

Roberts-Gordon	B-6	 60,000	   20' 	35'

Roberts-Gordon	B-8	 80,000	   20'	45'

Roberts-Gordon	B-9	 90,000	   25'	50'

Roberts-Gordon	B-10	 100,000	   30'	60'

Roberts-Gordon	B-12	 120,000	   35'	70'

Roberts-Gordon	B-12A	 110,000	   35'	70'